SPECIFICATIONS                                                                                                                                Triple Duty Valve – Model 3DV

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

# SECTION 23 05 93

Testing, Adjusting, and Balancing for HVAC

PART 1 GENERAL

1.01       SECTION INCLUDES

# Unit shall be a Bell & Gossett Triple Duty Valve, as manufactured by Xylem.

# Furnish Triple Duty Valve with capabilities as indicated in the plans.

1.02       RELATED SECTIONS

- Section 23 01 70 – Operation & Maintenance of Central HVAC Equipment

- Section 23 08 00 – Commissioning of HVAC

- Section 23 05 23 – General Duty Valves for HVAC Piping

- Section 23 20 00 – HVAC Piping and Pumps

- Section 23 21 13 – Hydronic Piping

- Section 23 21 16 – Hydronic Piping Specialties

- Section 23 21 23 – Hydronic Pumps

- Section 23 21 23.13 – In-Line Centrifugal Hydronic Pumps

- Section 23 21 23.16 – Base-Mounted, Centrifugal Hydronic Pumps

- Section 23 21 23.19 – Vertical-Mounted, Double-Suction Centrifugal Hydronic Pumps

1.03       REFERENCES

- ANSI – American National Standards Institute..

- ISO – International Standards Organization.

1.04       SUBMITTALS

- Submit data cover sheet.

- Dimensional print(s).

- Sales bulletin.

- Installation, operation & maintenance manual.

1.05      QUALITY ASSURANCE

- The product manufacturer shall be fully certified by the International Standards Organization 
per ISO 9001.

# The manufacturer shall carry a minimum product liability insurance of $5,000,000.00 per occurrence.

1.06      MAINTENANCE MATERIAL SUBMITTALS

PART 2 PRODUCTS

2.01      MANUFACTURERS

# Subject to compliance with these specifications, the following manufacturers shall be acceptable:

- Triple Duty Valve

- Xylem Inc. Bell & Gossett Model 3DV-____NMF or 3DV-____RFF.

- Pre-approved equal.

2.02      COMPONENTS

- Triple Duty Valve

- The valve shall be a straight pattern, non-adjustable design.

- The valve shall be a calibrated ball valve design.

- The valve shall have a MNPT threaded or rotatable flange inlet connection and a FNPT threaded outlet connection.

- The valve shall include a spring-loaded check valve to prevent gravity circulation and backflow.

- The valve shall have a calibrated nameplate with memory stop to allow the valve to be re-set to its balanced position after shut-off.

- The valve shall be capable of complete shut-off under pressure.

- The valve shall have an extended handle and extended pressure/temperature ports.

- The valve body shall be made of brass.

- The valve ball shall be made of chrome plated brass.

- The check valve body shall be made of glass filled Noryl.

- The check valve spring shall be made of stainless steel.

- The check valve seals shall be EPDM rubber.

- The valve shall be rated for 200 psi (1,378 kPa) maximum operating pressure.

- The valve shall have a temperature range of -4°F (-20°C) to 250°F (120°C).

2.03      ACCESSORIES

- Triple Duty Valve Accessories

- Pressure/Temperature port.

PART 3 EXECUTION

  - INSTALLATION

- Install Triple Duty Valve in accordance with manufacturer’s instructions.

- Unit shall be a Bell & Gossett Triple Duty Valve Model 3DV-____NMF or 3DV-____RFF as manufactured by Xylem.

###### END OF SECTION

www.bellgossett.com

Bell & Gossett is a trademark of Xylem Inc. or one of its subsidiaries.

© 2016 Xylem Inc.   Triple Duty Valve – Model 3DV  August 2016